## Room zone data
| PhD Study data_Mechanical System Characterisation_22&23 November 2016 | [9 empty] | (External C02 @ KDH = 377ppm) (External CO2 @ MP = 340ppm)
Hospital Mechanical Characterisation
Room | Hspl | Test | Micro Zone | Room dims (msq) | Volume Calc Test | Room volume | Occupancy | Vent type | Flow (L/s) | Temp @ supply (External) | Co2 @ supply/ outdoor | Temp @ room (internal) | Co2 @ return | ACH CO2 | corrected ACH | corrected Avg ACH of room | corrected Avg L/s of room | corrected L/s per person | L/s/p Lower Bound (error) | L/s/p Upper Bound (error) | corrected Avg L/s per person | Humidity | Window status | Comments
Triage Consult 1 | KDH | 1 | Z1 | 3.4X3.4X2.6 = 30.05 | 30.056 | 30.05 | 3 | Supply | 90 | 25 | 361 |  | 517 | 12.28 | 11.6729 | 11.6729 | 97.4359 | 32.4786 | 19.7917 | 90.4762 | 32.4786 | 55 | none
Triage Consult 2 | KDH | 4 | Z2 | 3.4X3.4X2.6 = 30.05 | 30.056 | 30.05 | 2 | Supply | 79.64 | 25.5 | 356 | 25.5 | 453 | 13.89 (13.89) | 12.5152 | 12.5152 | 104.4674 | 52.2337 | 25.7191 | N/A | 52.2337 | 57 | none
Triage waiting | KDH | 2 | - | 4.9X3.5X3.1 = 53.16 | 53.165 | 53.16 | 3 | Supply | 75.66 | 25.3 | 376 | 25 | 519 | 6.86 (4.53) | 7.1982 | 15.1463 | 97.4359 | 35.4312 | 20.8505 | 117.8295 | 42.0746 | 54.6 | Top light, closed permanent | Large top volume space connected to test 3 area and passage
Triage waiting | KDH | 3 | Z3 | 4.9X3.5X3.1 = 53.16 | 53.165 | 53.16 | 7 | Supply | 112.11 | 25.5 | 382 | 25.4 | 486 | 20.22 (13.36) | 23.0943 |  |  | 48.7179 | 24.8366 | 1266.6667 |  | 55.4 | Top light, closed permanent | Large top volume space connected to test 2 area and passage
Nurse Station | KDH | 5 | Z6 | 11.31X12.37X2.6 + (6.5X6.2X2.1 high volume atrium) = 448.38 | 448.3822 | 448.38 | 7 | Supply | 116.42 | 25.7 | 367 | 25.5 | 391 | 4.9 (10.1) | 11.8649 | 11.8649 | 1477.7778 | 211.1111 | 40.8602 | N/A | 211.1111 | 53.5 | Top light, closed permanent | Large volume multiple supply and extraction
|  | 6 | Z6 | 11.31X12.37X2.6 + (6.5X6.2X2.1 high volume atrium) = 448.38 | 448.3822 | 448.38 | 7 | Supply | 317.67 | 25.7 | 367 | 25.5 | 391 | 4.9 (10.1) | 11.8649 |  |  | 211.1111 | 40.8602 | N/A |  | 53.5 | Top light, closed permanent | Large volume multiple supply and extraction
|  | 7 | Z6 | 11.31X12.37X2.6 + (6.5X6.2X2.1 high volume atrium) = 448.38 | 448.3822 | 448.38 | 7 | Supply | 185.87 | 25.7 | 367 | 25.5 | 391 | 4.9 (10.1) | 11.8649 |  |  | 211.1111 | 40.8602 | N/A |  | 53.5 | Top light, closed permanent | Large volume multiple supply and extraction
|  | 7(2) | Z6 | Large open plan central atrium | #VALUE! |  | 7 | Supply | <10 | 0 | 0 | 0 | 0 | 3.7 | [7 empty] | 0 |  | Supply was not working
Resus | KDH | 8 | Z4 | 6.17X12.5X2.6 = 200.52 | 200.525 | 200.52 | 10 | Supply | 158.2 | 26 | 341 | 26 | 356 | 7.9 (Co2 <377) | 60.6423 | 62.4888 | 3480.6268 | 337.7778 | 44.058 | N/A | 348.0627 | 52.5 | All top hung open 20%
|  | 9 | Z4 | 6.17X12.5X2.6 = 200.52 | 200.525 | 200.52 | 10 | Supply | 163.74 | 26.2 | 343 | 26 | 356 | 7.9 (Co2 <377) | 69.9719 |  |  | 389.7436 | 44.8378 | N/A |  | 52.5 | All top hung open 20%
|  | 10 | Z4 | 6.17X12.5X2.6 = 200.52 | 200.525 | 200.52 | 10 | Supply | 118.39 | 26.2 | 340 | 26 | 356 | 7.9 (Co2 <377) | 56.8522 |  |  | 316.6667 | 43.6782 | N/A |  | 52.5 | All top hung open 20%
Nebulisation | KDH | 12 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 69.59 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 | 50.7117 | 1900 | 211.1111 | 40.8602 | N/A | 211.1111 | 51.7 | All top hung open 20%
|  | 13 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 33.21 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 |  |  | 211.1111 | 40.8602 | N/A |  | 51.7 | All top hung open 20%
|  | 14 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 58.57 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 |  |  | 211.1111 | 40.8602 | N/A |  | 51.7 | All top hung open 20%
|  | 15 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 71.97 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 |  |  | 211.1111 | 40.8602 | N/A |  | 51.7 | All top hung open 20%
|  | 16 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 37.47 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 |  |  | 211.1111 | 40.8602 | N/A |  | 51.7 | All top hung open 20%
|  | 17 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | 45.71 | 26.3 | 360 | 26.3 | 384 | 8.4 (55.7) | 50.7117 |  |  | 211.1111 | 40.8602 | N/A |  | 51.7 | All top hung open 20%
|  | 18 | Z7 | 8.17X6.35X2.6 = 134.88 | 134.8867 | 134.88 | 9 | Exhaust | - | [14 empty] | Not meaured due to patient privacy
Procedure 1 | KDH | 23 | Z8 | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 2 | Supply | 77.64 | 21.6 | 346 | 22 | 399 | 15.4 (14.89) | 10.0762 | 12.64 | 239.8444 | 95.5975 | 33.1155 | N/A | 119.9222 | 64 | none
|  | 24 | Z8 | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 2 | Supply | 76.65 | 21.2 | 344 | 22 | 385 | 15.4 (23.58) | 13.0253 |  |  | 123.5772 | 35.9338 | N/A |  | 64 | none
|  | 25 | Z8 | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 2 | Supply | 74.56 | 20.7 | 344 | 22 | 385 | 15.4 (23.58) | 13.0253 |  |  | 123.5772 | 35.9338 | N/A |  | 64 | none
|  | 26 | Z8 | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 2 | Supply | 62.95 | 20.4 | 348 | 22 | 385 | 15.4 (23.58) | 14.4334 |  |  | 136.9369 | 36.983 | N/A |  | 64 | none
Procedure 2 | KDH | 19 | - | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 5 | Supply | 21.97 | 22 | 358 | 24.5 | 420 | 9.1 (23.98) | 21.5337 | 25.1515 | 477.2497 | 81.7204 | 31.2757 | N/A | 95.4499 | 56.4 | none
|  | 20 | - | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 5 | Supply | 107 | 23.4 | 344 | 24.5 | 440 | 9.1 (17.91) | 13.9072 |  |  | 52.7778 | 25.8503 | N/A |  | 56.4 | none
|  | 21 | - | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 5 | Supply | 13.77 | 23 | 408 | 24.5 | 448 | 9.1 (16.26) | 33.3773 |  |  | 126.6667 | 36.1905 | N/A |  | 56.4 | none
|  | 22 | - | 4.53X5.80X2.6 = 68.31 | 68.3124 | 68.31 | 5 | Supply | 30.08 | 22.8 | 406 | 24.5 | 448 | 9.1 (16.26) | 31.7879 |  |  | 120.6349 | 35.6808 | N/A |  | 56.4 | none
Trolley (1) Main | KDH | 28 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 164.25 | 23.6 | 466 | 25.4 | 510 | 12.9 (9.2) | 22.9984 | 18.2131 | 2957.6568 | 115.1515 | 35.1852 | N/A | 89.786 | 54.1 | 70% top hung open @ 25%
|  | 29 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 161.6 | 24.2 | 466 | 25.4 | 554 | 12.9 (9.2) | 11.4992 |  |  | 57.5758 | 26.9504 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 30 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 260.87 | 24.5 | 466 | 25.4 | 480 | 12.9 (9.2) | 72.2806 |  |  | 361.9048 | 44.4444 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 31 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 222.03 | 24.8 | 466 | 25.4 | 512 | 12.9 (9.2) | 21.9984 |  |  | 110.1449 | 34.7032 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 32 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 198.25 | 24.9 | 466 | 25.4 | 524 | 12.9 (9.2) | 17.447 |  |  | 87.3563 | 32.0675 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 33 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 157.25 | 25 | 466 | 25.4 | 671 | 12.9 (9.2) | 4.9362 |  |  | 24.7154 | 16.612 | 48.254 |  | 54.1 | 70% top hung open @ 25%
|  | 34 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 193.77 | 25.1 | 466 | 25.4 | 525 | 12.9 (9.2) | 17.1513 |  |  | 85.8757 | 31.8658 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 35 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 185.9 | 25.1 | 466 | 25.4 | 563 | 12.9 (9.2) | 10.4322 |  |  | 52.2337 | 25.7191 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 36 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 173.67 | 25.1 | 466 | 25.4 | 537 | 12.9 (9.2) | 14.2525 |  |  | 71.3615 | 29.6296 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 37 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 174.58 | 25.2 | 466 | 25.4 | 532 | 12.9 (9.2) | 15.3322 |  |  | 76.7677 | 30.5221 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 38 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 177.8 | 25.3 | 466 | 25.4 | 509 | 12.9 (9.2) | 23.5332 |  |  | 117.8295 | 35.4312 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 39 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 144.77 | 25.2 | 466 | 25.4 | 520 | 12.9 (9.2) | 18.7394 |  |  | 93.8272 | 32.9004 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 40 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 32 | Exhaust | 178 | 25.2 | 466 | 25.4 | 529 | 12.9 (9.2) | 16.0623 |  |  | 80.4233 | 31.0838 | N/A |  | 54.1 | 70% top hung open @ 25%
|  | 41 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 36 | Large vertical Suppy grills 890x1.182mm @ 0.49m/sec | 515 | 25.7 | 360 | 25.4 | 466 | 6.5 (9.22) | 10.7398 |  |  | 47.7987 | 24.5955 | 844.4444 |  | 54.1 | Top light, closed permanent | Sonic liner in ducts
|  | 42 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 36 | Large vertical Suppy grills 890x1.182mm @ 0.19m/sec | 199 | 25.9 | 360 | 25.4 | 466 | 6.5 (9.22) | 10.7398 |  |  | 47.7987 | 24.5955 | 844.4444 |  | 54.1 | Top light, closed permanent | Sonic liner in ducts
|  | 43 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 36 | Large vertical Suppy grills 890x1.182mm @ 0.02m/sec | 21 | 26.1 | 360 | 25.4 | 466 | 6.5 (9.22) | 10.7398 |  |  | 47.7987 | 24.5955 | 844.4444 |  | 54.1 | Top light, closed permanent | Sonic liner in ducts
|  | 44 | Z9 | 11.83X17.30X2.6 (5.60X3.80X2.1 Large open plan) = 576.80 | 576.8014 | 576.8 | 36 | Large vertical Suppy grills 890x1.182mm @ 0.30m/sec | 315 | 26.2 | 360 | 25.4 | 466 | 6.5 (9.22) | 10.7398 |  |  | 47.7987 | 24.5955 | 844.4444 |  | 54.1 | Top light, closed permanent | Sonic liner in ducts
Trolley (1) Main+Neb | MP | 45 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 50 | Supply | 119.73 | 22.6 | 360 | 22 | 430 | 5.8 (20.98) | 30.6974 | 19.3804 | 2244.1254 | 72.381 | 29.8039 | N/A | 79.9853 | 56 | 60% top hung open @ 25%
|  | 46 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Supply | 154.93 | 22.1 | 360 | 22 | 470 | 5.8 (13.28) | 14.065 |  |  | 46.0606 | 24.127 | 506.6667 |  | 56 | 60% top hung open @ 25%
|  | 47 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Supply | 122 | 22 | 361 | 22 | 460 | 5.8 (14.62) | 15.6277 |  |  | 51.1785 | 25.4606 | N/A |  | 56 | 60% top hung open @ 25%
|  | 48 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Supply | 145.93 | 21.5 | 360 | 22 | 461 | 5.8 (14.48) | 15.3183 |  |  | 50.165 | 25.2073 | 5066.6667 |  | 56 | 60% top hung open @ 25%
|  | 49 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Supply | 141.73 | 21.2 | 360 | 22 | 433 | 5.8 (20.11) | 21.1938 |  |  | 69.4064 | 29.2871 | N/A |  | 56 | 60% top hung open @ 25%
|  | 66 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 105.94 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 | 28.6509 | 3377.7778 | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 67 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 99.9 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 68 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 121.92 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 69 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | - | - |  | - | - | [8 empty] | - |  | Exhaust was not working
|  | 70 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | - | - |  | - | - | [8 empty] | - |  | Exhaust was not working
|  | 71 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | - | - |  | - | - | [8 empty] | - |  | Exhaust was not working
|  | 72 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | - | - |  | - | - | [8 empty] | - |  | Exhaust was not working
|  | 73 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 135.3 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 74 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 129.46 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 75 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 109.76 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 76 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 66.6 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
|  | 77 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | - | [14 empty] | Not meaured due to patient privacy
|  | 78 | Z9 (1)+(2) | 10.6X15.4X2.6 = 424.42 (Large open plan) | 424.424 | 424.42 | 36 | Exhaust | 78.01 | n/a | 360 | 23 | 414 | 5.8 (27.31) | 28.6509 |  |  | 93.8272 | 32.9004 | N/A |  | 60.4 | 60% top hung open @ 25%
Nurse Station | MP | 50 | Z6 | 10.5X7.1X2.6 (3.9X5.7X2.1 high volume atrium) = 239.68 | 240.513 | 239.68 | 9 | Supply | 154.45 | 22.9 | 360 | 22 | 460 | 6.2 (7.32) | 6.8491 | 9.5273 | 634.3077 | 50.6667 | 25.3333 | N/A | 70.4786 | 56 | Top light, closed permanent
|  | 51 | Z6 | 10.5X7.1X2.6 (3.9X5.7X2.1 high volume atrium) = 239.68 | 240.513 | 239.68 | 9 | Supply | 140.25 | 21.6 | 360 | 22 | 412 | 6.2 (14.20) | 13.1714 |  |  | 97.4359 | 33.3333 | N/A |  | 56 | Top light, closed permanent
|  | 52 | Z6 | 10.5X7.1X2.6 (3.9X5.7X2.1 high volume atrium) = 239.68 | 240.513 | 239.68 | 9 | Supply | 123.81 | 21.4 | 360 | 22 | 440 | 6.2 (9.17) | 8.5614 |  |  | 63.3333 | 28.1481 | N/A |  | 56 | Top light, closed permanent
Psych/Psych | MP | 62 | - | 4.02X6.48X2.6 = 67.73 | 67.729 | 67.73 | 5 | Exhaust | 636 | n/a | 360 | 23.8 | 400 | 33.8 (36.34) | 33.6631 | 33.6631 | 126.6667 | 126.6667 | 36.1905 | N/A | 130 | 63.8 | none
|  | 63 | - | 4.02X6.48X2.6 = 67.73 | 67.729 | 67.73 | 5 | Supply | 13.4 | 24.4 | 357 | 24.7 | 395 | 0.7 (41.69) | 35.4348 | 35.4348 | 133.3333 | 133.3333 | 36.715 | N/A |  | 63.8 | none
Resus | MP | 53 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 8 | Supply | 114.31 | 22.4 | 360 | 22.7 | 610 | 10.07 (2.90) | 2.7453 | 4.6331 | 273.6261 | 20.2667 | 14.4762 | 33.7778 | 124.7575 | 62 | single top hung open @ 25%
|  | 54 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 8 | Supply | 96.34 | 22.3 | 360 | 22.7 | 616 | 10.07 (2.83) | 2.681 |  |  | 19.7917 | 14.2322 | 32.4786 |  | 65 | single top hung open @ 25%
|  | 55 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 8 | Supply | 102.87 | 22.1 | 363 | 22.7 | 444 | 10.07 (8.70) | 8.4732 |  |  | 62.5514 | 27.9926 | N/A |  | 65 | single top hung open @ 25%
|  | 62 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 8 | Exhaust | 106.7 | n/a | 360 | 23.7 | 376 | 13.8 (48.16) | 42.8954 | 22.2555 | 1252.3755 | 316.6667 | 43.6782 | N/A |  | 60.5 | single top hung open @ 25%
|  | 63 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 6 | Exhaust | 158.91 | n/a | 360 | 23.6 | 388 | 13.8 (20.07) | 18.3838 |  |  | 180.9524 | 39.5833 | N/A |  | 60.5 | single top hung open @ 25%
|  | 64 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 6 | Exhaust | 308.96 | n/a | 360 | 23.5 | 388 | 13.8 (20.07) | 18.3838 |  |  | 180.9524 | 39.5833 | N/A |  | 60.5 | single top hung open @ 25%
|  | 65 | Z7 | 6.3X12.98X2.6 = 212.61 | 212.6124 | 212.61 | 6 | Exhaust | 241.3 | n/a | 360 | 23.5 | 415 | 13.8 (10.03) | 9.359 |  |  | 92.1212 | 32.6882 | N/A |  | 60.5 | single top hung open @ 25%
Procedure 1 | MP | 56 | Z4 | 3.82X3.90X2.6 = 38.74 | 38.7348 | 38.74 | 2 | Supply | 75.93 | 22.8 | 362 | 24.3 | 394 | 7.05 (30.04) | 29.4269 | 29.4269 | 158.3333 | 158.3333 | 38.3838 | N/A | 158.3333 | 57 | none
Procedure 2 | MP | 57 | - | 3.82X3.90X2.6 = 38.74 | 38.7348 | 38.74 | 2 | Supply | 84 | 22.8 | 359 | 22.1 | 408 | 7.8 (21.09) | 19.2176 | 19.2176 | 103.4014 | 103.4014 | 34.0045 | N/A | 103.4014 | 61.2 | none
Triage waiting | MP | 58 | Z3 | 4.87X8.75X2.6 = 110.80 | 110.7925 | 110.8 | 9 | Exhaust | 139 | n/a | 360 | 23.2 | 420 | 7.5 (26.44) | 24.6931 | 18.134 | 558.125 | 84.4444 | 31.6667 | N/A | 62.0139 | 56 | none
|  | 59 | Z3 | 4.87X8.75X2.6 = 110.80 | 110.7925 | 110.8 | 9 | Exhaust | 94.04 | n/a | 360 | 23.2 | 488 | 7.5 (12.28) | 11.5749 |  |  | 39.5833 | 22.2222 | 180.9524 |  | 56 | none
Triage Consult 1 | MP | 60 | Z1 | 3.8X3.9X2.6 = 38.53 | 38.532 | 38.53 | 4 | Supply | 54.9 | 23.4 | 430 | 24.3 | 540 | 5.1 (11.13) | 17.2144 | 17.2144 | 46.0606 | 46.0606 | 24.127 | 506.6667 | 46.0606 | 57 | none
Triage consult 2 | MP | 61 | Z2 | 3.8X3.9X2.6 = 38.53 | 38.532 | 38.53 | 3 | Supply | 55 | 23.7 | 360 | 23.2 | 432 | 5.13 (28.07) | 19.7249 | 19.7249 | 70.3704 | 70.3704 | 29.4574 | N/A | 70.3704 | 58.7 | none
[16 empty] | 24.0156 | 130

## Sheet3
breathing rate | 8 | L/min | L/s/perons | 220.2899
CO2 outdoor | 361 | PPM
C Breath | 38000 | PPM
C Room | 384 | PPM